Sefton Adult Learning Service
Industrial and Machine control systems
Presented
By Tony McDonald
Class 10 Time and Temperature Measurement

---
Analogue Measurements
1. Many sensors involve a control voltage proportional to a measurement value. From unit 3 we learned that:
3. Some devices or instruments use an analogue output to transmit data to another controller. For example some thermocouple interface devices send the output in either voltage or current modes. These are normally either 0-10 volts +/-10Volts 0-2 volts or in the current mode 0-20 mA or 4 to 20mA.
Current is preferred to voltage as constant current output automatically compensate for noise that has been picked up in cables etc. The current from the sensor is applied to a resistor, that is also grounded. Therefore the voltage is generated across the resistor. Ultimately the measurement needs to be represented by a voltage.
Many precision measurements in instrumentation use analogue signals. Examples of such measurements include:
- Temperature.
- Pressure.
- Load/Weight.
- Light intensity.
- PH.
- Colour.

---
Analogue Measurements
1. We are going to study temperature measurements these tend to be to most common measurements made in industry.
3. There are various common techniques that are used to measure temperature. These are listed below:
- Platinum resistance (PT100).
- Thermistors.
- Thermocouple.
- Silicon Diodes.
- Semiconductor sensors.
- Irfa red.
2. Of these the PT100 is known to be precision but is not linear the temperature sensing range is roughly -200 to 600'C. At 0'C the resistance is 100 ohms (hence the name PT100) at 600'C it has a resistance of 313.59 Ohms. At -200'C the resistance is 18.49 ohms. To use the full range of a PT100 sensor, the reading device must use a linearising technique, this normally involves a digital look up table where a voltage is read from the sensor and referred to look up table to correct the reading.

---
Thermocouple:
10. Thermocouples are basically just two wires welded together. There are two junctions on these devices these are the hot junction and the cold junction. The device provides a voltage equivalent to the temperature difference between the hot and cold junctions. This voltage is very low at around about 20uV per degree Celsius. Because the device is differential it needs to be compensated to read ambient temperature, this is called cold junction compensation. Thermocouples need linearisation over the full range, but present ranges that are almost linear and can be used over a short range without linearisation.
12. Thermocouples use an amplifier to boost the Thermocouple signal to a level that useable for the analogue digital converter that is needed for the signal to be digitised and useable in a computer.

---
Analogue Measurements
Thermistors:
Are a non linear resistor that displays a different resistance to different temperature stimulus. Thermistors are available in negative and positive temperature coefficients (NTC or PTC). These devices don't tend to be used in industrial applications but are commonly found in cheap thermometers. Thermistors have non linear characteristics and need to be linearised
1. Diodes:
2. Transistors and diodes have a PN forward bias voltage that changes with temperature, this voltage is linear. The voltage is around 700mV at room temperature and changes by 2.2mV per degrees Celsius. The useful range is -50 to 200 'C.
5. Semiconductor Sensors:
6. Provide a linear voltage or current change per temperature for a change in temperature. Many devices are laser trimmed and are extremely accurate. Devices normally output a voltage often 10mV per Kelvin or constant current.
8. Infra Red:
9. Infra red sensors are fast and can read a temperature of a remote surface. In industrial applications they are commonly used for measuring the temperature of rollers, and items that are difficult to fix a sensor on.

---
Signal converters
1. Signal converters are devices that covert the low signal voltages to a current or voltage that the control system can use. Converters often output 4 to 20 ma. Converters contain all the circuitry needed to interface the sensor. If the converter is used for thermocouples then the device must include a cold junction compensation.
Measurement standards:
Some devices or instruments use an analogue output to transmit data to another controller. For example some thermocouple interface devices send the output in either voltage or current modes. These are normally either 0-10 volts +/-10Volts 0-2 volts or in the current mode 0-20 mA or 4 to 20mA.
Current is preferred to voltage as constant current output automatically compensate for noise that has been picked up in cables etc.

---
Time Measurement
1. In computers there are normally two clocks these are the system clock and the real-time clock. The real-time clock is a device that records the time of day et cetera.
3. Real Time Clock:
4. Normally these devices use watch crystal that operates at a frequency of 32,768 Hz. The device continues to run when the computer is switched off and normally has its own battery supply. The time can sometimes be resolved down to hundreds of the second although many real-time clocks support the second as the smallest unit of time. Some real-time clocks only provide a 24-hour clock (this is preferred by most programmers) however some can also provide a 12 hour clock with an AM PM indicator. Most real-time clocks provide seconds, minutes, hours, days, weekday, month and years. Some are even capable of updating themselves during the year.
6. In many programs the real-time misrepresented as a compressed structure and normally in a long for example the time computer file is represented as the number of half minutes (30 seconds) since 1989. More modern computers like the pmc4 use the number of seconds at a past since the year 2000.
8. System Clock:
9. A computers clock is actually used as a source to synchronise memory and other activities. A clock is required normally to ensure that all signals have sufficient time to propagate to the required logic level before they have been read or written.

---
Time Measurement
Timers:
Timers are normally a device that operates from the system clock often the most useful time will be in milliseconds (1000th of a second). Map makes a timer group available to the programmer these work in milliseconds. Timers are based upon a hardware timer which counts the number of pulses provided by the clock to deliver a preset timing interval when this interval has been achieved and interrupt is generated and the clock timer is reset. This is one of the most common techniques used in programming and is generally a low-level task run by the operating system. Map like many other programs provides a timer that gives the number of milliseconds since the controller was switched on this is particularly useful timing short time loops. Normally the real-time clock will not be involved in timing activity as it is not fast enough and cannot return the number of milliseconds. Sometimes data is recorded over many months or years in which case the real-time clock would be the obvious choice for this type of data recording.
Data logging:
Data logging involves monitoring data at a fixed time interval. In years gone by chart recorders were common whereby a rotary chart moved slowly and an ink pen moved up and down depending upon the the measurement being taken normally temperature. This is important in many applications such as the medical industry where it is necessary to keep a record of temperatures that have been achieved over time profile. In modern equipment we record the measurements every Sample period. Normally temperature does not move very rapidly and therefore the Sample period can be around 60 seconds or more.

---
Time Measurement
Data logging In Map:
There are three commands that mainly control data logging in map these are listed below:
LogTask (start a data logger task)
MAP LogTask command data logger function it is designed to start the logging task and is called from MAP Therefore it has to allocate memory for the results and Start the timer.
Data field usage:
Data[0] is the channel number of the ADC or axis..
Data[1] is the number of analogue data samples that are to be averaged.
Startlog (start the data logging process)
This function is the MAP data logger function it is designed to start the logging task and is called from MAP Therefore it has to allocate memory for the results and Start the timer.
Data field usage:
Data[0] is the number of samples in unsigned long
Data[1] is a constant float or register number representing the Sample period in seconds float minimum is 0.01 seconds.

---
Time Measurement
Data logging In Map continued:
Stoplog (stop the data logging)
This function is the MAP data logger stop function it is designed to stop the logging task and write the result to the flash stick is called from MAP it will if successful it will delete the allocated memory the timer is stopped. The data fields are not used by the command itself and therefore are available for a 16 character comment. The message is displayed only in the edit mode, does nothing during simulation or on the screen during run.